# Commissioning protocol

Company

Responsible

| Customer | Date | Installation |
| --- | --- | --- |
| Object/Unit | Item no. | Installation address |
| Model/size | Series no. |  |

Filter replace pressure set.

Present time and date set.

Week scheduler settings

Preset On-time is:

Period 1. 07:00-16:00 Monday-Sunday, Medium fan-speed.

Period 2. 00:00-00:00 Monday-Sunday. 00:00-00:00 inactivates the period.

Preset Off time is:

Remaining time: Low fan-speed.

| Weekday | Period | Running times (On) |
| --- | --- | --- |
| Monday | 1 | : - : |
|  | 2 | : - : |
| Tuesday | 1 | : - : |
|  | 2 | : - : |
| Wednesday | 1 | : - : |
|  | 2 | : - : |
| Thursday | 1 | : - : |
|  | 2 | : - : |
| Friday | 1 | : - : |
|  | 2 | : - : |
| Saturday | 1 | : - : |
|  | 2 | : - : |
| Sunday | 1 | : - : |
|  | 2 | : - : |

Running mode On: Low ,   High

Running mode Off  (remaining time): Shut off ,  Low ,  High

| Function | Preset value | Set value |
| --- | --- | --- |
| Temperature |  |  |
| Control function Temp. | Supply Supply outdoor Exhaust | Supply Supply outdoor Exhaust |
| Control Temp. | xx °C | °C |
| Outdoor compensating |  |  |
| Outdoor temp. -20,0 °C | Compensation: 20,0 °C | °C |
| +15,0 °C | Compensation: 0,0 °C | °C |
| Min. supply set point | 12,0 °C | °C |
| Max. supply set point | 30,0 °C | °C |
| ###### Air flow |  |  |
| Fan speed Low | xx% of max. Fan speed | % |
| Fan speed Maximum | xxx% of max. Fan speed | % |
| Extended/Forced running |  |  |
| Running time | xxx Minutes *) | Minutes *) |
| ###### Filter alarm |  |  |
| Replace pressure | xxx Pa | Pa |
| ###### Cooling |  |  |
| Status | Not active | Active |
| ###### Cool Recycling |  |  |
| Status | Not active | Active |
| Free Cooling |  |  |
| Status | Not active | Active |
| Outdoor temp activation: | xx°C | °C |
| Outdoor temp night: | High: 15°C Low: 5°C | High: °C Low: °C |
| Room temp min: | 18°C | °C |
| ###### Fire function |  |  |
| Status | Not active | Active |
| Running mode at activated fire alarm | Unit shut off | High fan speed |

*) Set the minutes to 0 when using an external Timer.